## Slide 1
ELECTROTECHNOLOGY | SECTION 10
Selecting devices for
isolation and switching
A workbook-guided lesson / AS/NZS 3000:2018 + A1–A3 + Ruling 1
FIND THE RULE • EXPLAIN THE RISK • JUSTIFY THE DEVICE
Notes: Teacher copy: slides contain prompts and no pre-filled workbook answers. Speaker notes contain guidance and corrections. Do not distribute notes to students.

## Slide 2
SECTION 10 / WIRING RULES
02
HOW TO USE THIS PRESENTATION
The rulebook is the source
The workbook is the route through the lesson. This deck provides cues, not a completed answer sheet.
01
LOOK UP
Open the nominated AS/NZS 3000 clause.
02
DECIDE
Identify the rule, exception or limiting condition.
03
EXPLAIN
Describe the safety reason in your own words.
04
RECORD
Fill in the workbook after discussion.
Notes: Encourage students to physically locate the clause and identify requirements versus notes, examples and exceptions. Workbook numbering reflects older editions and includes errors.

## Slide 3
SECTION 10 / WIRING RULES
03
LESSON MAP
Five decisions electricians make
Move from isolation principles to selecting a device for a real installation.
01
What must be isolated?
Activities 1–8
02
Who needs to disconnect it?
Activities 9–21
03
What equipment needs local isolation?
Activities 22–28
04
Could the machine injure someone?
Activities 29–36
05
Will the device perform the duty?
Activities 37–44

## Slide 4
SECTION 10 / WIRING RULES
04
01
FOUNDATIONS
Control is not always isolation
What does the switching device actually make safe?
Notes: Ask students for a practical example before advancing to the clause-specific activities.

## Slide 5
SECTION 10 / WIRING RULES
05
ACT 01
Purpose of control and isolation
WORKBOOK PROMPTS
Why must equipment be capable of being disconnected?
Which dangers are we trying to prevent?
◎
FIND THIS CLAUSE
1.5.2
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 1 — Purpose of control and isolation Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 1.5.2. Instructor note: Clause 1.5.2 addresses control/isolation for hazards and maintenance, isolation from external sources, separation of safety service controls, and isolating all active conductors.

## Slide 6
SECTION 10 / WIRING RULES
06
ACT 02
Design for safe maintenance
WORKBOOK PROMPTS
How could a fault interrupt more equipment than necessary?
What design choice might reduce inconvenience?
◎
FIND THIS CLAUSE
1.6.1(e)
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 2 — Design for safe maintenance Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 1.6.1(e). Instructor note: The workbook highlights item (e): reduce inconvenience in the event of a fault. Other design aims include safe testing and maintenance.

## Slide 7
SECTION 10 / WIRING RULES
07
ACT 03
Choosing switching equipment
WORKBOOK PROMPTS
Which jobs must switchgear and controlgear perform?
Can one device carry out more than one function?
◎
FIND THIS CLAUSE
2.1.2
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 3 — Choosing switching equipment Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.1.2. Instructor note: Discuss isolation/control, automatic disconnection, abnormal voltage and equipment grouping. Note 2.2.4.1: multifunction devices must meet each applicable requirement.

## Slide 8
SECTION 10 / WIRING RULES
08
ACT 04
Four different switching functions
WORKBOOK PROMPTS
Can a device intended for everyday control be assumed to isolate?
Name the functions listed in the clause.
◎
FIND THIS CLAUSE
2.3.1
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 4 — Four different switching functions Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.1. Instructor note: Four functions: isolation (2.3.2.2); emergency (2.3.5.2); mechanical maintenance (2.3.6.2); functional control (2.3.7.2). A device with multiple functions must satisfy each.

## Slide 9
SECTION 10 / WIRING RULES
09
ACT 05
Preventing unexpected energisation
WORKBOOK PROMPTS
Find three precautions against inadvertent energisation.
What additional action should be needed to re-energise?
L
FIND THIS CLAUSE
2.3.2.1.1
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 5 — Preventing unexpected energisation Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.2.1.1. Instructor note: Correct ref 2.3.2.1.1, not merely 2.3.2.1. Notes suggest padlocks, warning notices, lockable enclosures. Short-circuiting and earthing is supplementary only.

## Slide 10
SECTION 10 / WIRING RULES
10
ACT 06
AC circuits: what is switched?
WORKBOOK PROMPTS
In a three-phase AC circuit, which conductors must be isolated?
What are the neutral and PEN restrictions?
~
FIND THIS CLAUSE
2.3.2.1.2
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 6 — AC circuits: what is switched? Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.2.1.2. Instructor note: Correction: original gives 2.3.2.1.1, but AC-specific rule is 2.3.2.1.2. All active conductors isolated. No neutral switch in consumer mains or PEN; switched neutrals in other circuits have linked active poles and switching sequence. Never switch PE or PEN.

## Slide 11
SECTION 10 / WIRING RULES
11
ACT 07
DC circuits: identify the exceptions
WORKBOOK PROMPTS
Which conductors need isolation in a DC circuit?
When can fewer conductors be switched?
=
FIND THIS CLAUSE
2.3.2.1.3
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 7 — DC circuits: identify the exceptions Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.2.1.3. Instructor note: Correction: original gives 2.3.2.1.2, but DC rule is 2.3.2.1.3. All conductors, except an earthed conductor need not be switched; ELV DC may switch one fewer conductor under clause 7.5.8.2(b).

## Slide 12
SECTION 10 / WIRING RULES
12
ACT 08
What makes a device an isolator?
WORKBOOK PROMPTS
Why is solid-state switching inadequate for isolation?
How is OFF shown reliably?
Can every isolator interrupt current while carrying load?
◎
FIND THIS CLAUSE
2.3.2.2.1
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 8 — What makes a device an isolator? Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.2.2.1. Instructor note: Semiconductor-only devices are prohibited for isolation. An isolator must disconnect actives, reliably indicate open, avoid unintentional closure, and be readily available. Off-load disconnectors may be used only with measures preventing operation on load. Original answer load current unqualified and incorrect.

## Slide 13
SECTION 10 / WIRING RULES
13
EXPLAIN IT IN YOUR OWN WORDS
Same OFF position. Different safety effect.
Discuss what OFF means in each case.
LIGHT
Light switched off; live loop remains.
LOCKOUT
Supply separated for electrical work.
MOTOR
Moving parts cannot restart.
Notes: Switching functions differ. For electrical isolation apply clause 2.3.2.2 and verified safe isolation practice; for mechanical maintenance use 2.3.6.

## Slide 14
SECTION 10 / WIRING RULES
14
02
MAIN SWITCHES
Isolation in an emergency
Who can disconnect the supply — and what must remain energised?
Notes: Ask students for a practical example before advancing to the clause-specific activities.

## Slide 15
SECTION 10 / WIRING RULES
15
ACT 09
What counts as a safety service?
WORKBOOK PROMPTS
Find the definition of a safety service.
How is its purpose different from general building equipment?
◎
FIND THIS CLAUSE
1.4.104; 7.2.1.1
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 9 — What counts as a safety service? Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 1.4.104; 7.2.1.1. Instructor note: Workbook error: reference 1.4.82 defines MAIN SWITCH, not safety service. The correct safety service definition is 1.4.104. Use 7.2.1.1 for safety-service context.

## Slide 16
SECTION 10 / WIRING RULES
16
ACT 10
Main switches at an installation
WORKBOOK PROMPTS
Where must the general installation supply be controlled?
What changes if several supplies are present?
◎
FIND THIS CLAUSE
2.3.3.2
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 10 — Main switches at an installation Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.3.2. Instructor note: Original refers to 2.3.3.1 (introduction) but required rules in 2.3.3.2. Main switches on the main switchboard; exceptions apply to some alternative/supplementary supplies. Safety services separate.

## Slide 17
SECTION 10 / WIRING RULES
17
ACT 11
How many main switches?
WORKBOOK PROMPTS
Consider separately metered supplies. How many may be used?
What changes when one meter provides separate controlled supplies?
#
FIND THIS CLAUSE
2.3.3.3
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 11 — How many main switches? Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.3.3. Instructor note: Original refers to 2.3.3.2; correct number provision 2.3.3.3. Domestic: no more than one per separately metered supply, OR per separately controlled supply from one meter. Distinguish meters and controlled tariffs; avoid universal two-switch example.

## Slide 18
SECTION 10 / WIRING RULES
18
ACT 12
Diagram: general and safety services
WORKBOOK PROMPTS
Trace what opens when the general main switch operates.
Which essential services must remain supplied?
◎
FIND THIS CLAUSE
2.3.3.2; 7.2.4.2
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 12 — Diagram: general and safety services Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.3.2; 7.2.4.2. Instructor note: Original NSWSR page 4-19 figure 4.9 is superseded. Use AS/NZS 3000 7.2.4.2 and current NSW SIR (April 2026) for relevant arrangements. Confirm applicable service conditions for teaching.

## Slide 19
SECTION 10 / WIRING RULES
19
ACT 13
Main-switch location and access
WORKBOOK PROMPTS
What is the allowable operating height?
What is different about multi-occupier access?
Why is public-land equipment an exception?
~
FIND THIS CLAUSE
2.3.3.4
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 13 — Main-switch location and access Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.3.4. Instructor note: Original refers to 2.3.3.3; correct location is 2.3.3.4. Handle max 2m from ground/floor/platform; public land exception is conditional. Individual occupiers must have access unless main switch accessible.

## Slide 20
SECTION 10 / WIRING RULES
20
ACT 14
Marking a main switch
WORKBOOK PROMPTS
What words must appear on a main-switch label?
How do multiple supplies affect the label and notices?
ID
FIND THIS CLAUSE
2.3.3.5
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 14 — Marking a main switch Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.3.5. Instructor note: Original refers to 2.3.3.4; correct 2.3.3.5. Mark MAIN SWITCH, identify portion controlled, notices for alternative/multiple supplies, and supplementary/alternative source label. Original simplistic solar label not universally sufficient.

## Slide 21
SECTION 10 / WIRING RULES
21
VISUAL REASONING / SAFETY SERVICES
Trace the supply path
What must stay supplied after the general main switch is opened?
SUPPLY
SPLIT
GENERAL MS
SAFETY MS
GENERAL LOAD
SAFETY LOAD
Notice: this is a teaching concept diagram, not an installation drawing.
Notes: Safety service main switches are arranged supply side of general installation main switches under clause 7.2.4.2, with exceptions and specialised installation rules. Do not treat drawing as a construction guide.

## Slide 22
SECTION 10 / WIRING RULES
22
ACT 15
What is a safety service?
WORKBOOK PROMPTS
What is the safety purpose of these services?
Which systems in this building depend on staying energised?
◎
FIND THIS CLAUSE
7.2.1.1
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 15 — What is a safety service? Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 7.2.1.1. Instructor note: Section 7.2 refers to safety services. Original wording emergency systems is used in previous standards; distinguish mandatory systems according to NCC/AS 1670 etc.

## Slide 23
SECTION 10 / WIRING RULES
23
ACT 16
Separate safety-service controls
WORKBOOK PROMPTS
Why must safety-service switches be separate?
Could a general-installation fault disable a safety service?
◎
FIND THIS CLAUSE
7.2.3.1; 7.2.4.1
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 16 — Separate safety-service controls Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 7.2.3.1; 7.2.4.1. Instructor note: Correct overarching main switch separation requirements appear 7.2.4.1; switchboard general rules at 7.2.3.1. Main switches separate from general installation and other types of safety services.

## Slide 24
SECTION 10 / WIRING RULES
24
ACT 17
Number of safety-service switches
WORKBOOK PROMPTS
Which clause sets the number?
Why might several separate switches be needed?
#
FIND THIS CLAUSE
7.2.4.1
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 17 — Number of safety-service switches Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 7.2.4.1. Instructor note: Original incorrectly refers to 7.2.3.2 (switchgear). 7.2.4.1 states no limit on number of safety-service main switches.

## Slide 25
SECTION 10 / WIRING RULES
25
ACT 18
Arrangement of safety supplies
WORKBOOK PROMPTS
Sketch a supply path to general equipment and safety services.
Could the general switch interrupt the safety service?
◎
FIND THIS CLAUSE
7.2.4.2
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 18 — Arrangement of safety supplies Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 7.2.4.2. Instructor note: Original refers to 7.2.4.1 but arrangement is 7.2.4.2. Safety service switch connected upstream of general switches; controls only safety service equipment; exceptions exist, especially fire alarm/intercom.

## Slide 26
SECTION 10 / WIRING RULES
26
ACT 19
Identify safety-service switches
WORKBOOK PROMPTS
What would an emergency responder need to see?
Find the special fire warning marking.
◎
FIND THIS CLAUSE
7.2.4.4
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 19 — Identify safety-service switches Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 7.2.4.4. Instructor note: Major error: original cites 7.2.6.2 (fire/smoke detection equipment); correct 7.2.4.4. Main switches marked MAIN SWITCH + service, IN THE EVENT OF FIRE, DO NOT SWITCH OFF, and contrasting colour/other means.

## Slide 27
SECTION 10 / WIRING RULES
27
ACT 20
Isolation in outbuildings
WORKBOOK PROMPTS
Where must the outbuilding supply be switched?
What if two submains supply that outbuilding?
◎
FIND THIS CLAUSE
2.3.4.1
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 20 — Isolation in outbuildings Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.4.1. Instructor note: Original blanket statement granny flat separate installation lacks threshold nuance. 2.3.4.1 requires a switch at outbuilding board. Outbuilding treated as a separate installation if BOTH max demand >=100A/phase and a switchboard, under this subclause; do not confuse with building category.

## Slide 28
SECTION 10 / WIRING RULES
28
ACT 21
Submains and circuits above 100 A
WORKBOOK PROMPTS
At what point in the circuit is the extra isolating switch required?
When could a protective circuit-breaker perform isolation?
◎
FIND THIS CLAUSE
2.3.4.2
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 21 — Submains and circuits above 100 A Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.4.2. Instructor note: A separate isolating switch at switchboard origin for every submain/final subcircuit rated >100A/phase, with limited exception for teed-off small submains. A CB may count if meets isolator requirements. Do not label it MAIN SWITCH automatically.

## Slide 29
SECTION 10 / WIRING RULES
29
03
EQUIPMENT
Different loads, different rules
Find the appliance-specific isolation provision.
Notes: Ask students for a practical example before advancing to the clause-specific activities.

## Slide 30
SECTION 10 / WIRING RULES
30
ACT 22
Which equipment has special rules?
WORKBOOK PROMPTS
Make a list of appliances needing equipment-specific clauses.
Why is one general rule not enough?
◎
FIND THIS CLAUSE
2.3.4.5
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 22 — Which equipment has special rules? Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.4.5. Instructor note: This points the student to section 4 and 7: sockets, cooking, water/room heaters, heating cables, converters, motors, etc. Refer to precise subclauses below.

## Slide 31
SECTION 10 / WIRING RULES
31
ACT 23
Socket-outlet switching
WORKBOOK PROMPTS
Which conductors are switched?
When can one switch serve two outlets?
Which restricted outlet may omit a switch?
◯
FIND THIS CLAUSE
4.4.4.1–4.4.4.2
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 23 — Socket-outlet switching Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 4.4.4.1–4.4.4.2. Instructor note: General rule: each outlet individually controlled by a separate switch in all active conductors. Exception adjacent pair; not readily accessible <=10A fixed/stationary appliance or luminaire; insertion/withdrawal switched type. Original omitted <=10A qualification.

## Slide 32
SECTION 10 / WIRING RULES
32
ACT 24
Fixed cooking appliances
WORKBOOK PROMPTS
Which cooking surfaces require a local switch?
Where must a person reach to operate it?
What is different for combined gas/electric appliances?
◎
FIND THIS CLAUSE
4.7.1; 4.7.3
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 24 — Fixed cooking appliances Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 4.7.1; 4.7.3. Instructor note: Fixed open-surface appliances require nearby visible readily accessible switch in all actives, not on appliance. In Australia combined gas+electric open cooking requires switching all LIVE conductors (active and neutral). Enclosed ovens normally excluded. Location not across cooking surface.

## Slide 33
SECTION 10 / WIRING RULES
33
ACT 25
Direct-connected water heaters
WORKBOOK PROMPTS
Is the switchboard breaker sufficient?
Where must the independent lockable isolator be installed?
◎
FIND THIS CLAUSE
4.8.2.3
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 25 — Direct-connected water heaters Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 4.8.2.3. Instructor note: Critical correction. AS/NZS 3000:2018 A1 clause 4.8.2.3 requires an independent lockable isolating switch adjacent to BUT NOT ON a direct-connected water heater. Circuit-breaker at source alone is NOT an alternative. If multiple final subcircuits, all isolated by single isolating switch. Workbook answers give false choice.

## Slide 34
SECTION 10 / WIRING RULES
34
ACT 26
Room-heater isolation
WORKBOOK PROMPTS
Where can an isolation device be fitted?
Can a thermostat double as the isolation device?
◎
FIND THIS CLAUSE
4.9.2–4.9.3
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 26 — Room-heater isolation Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 4.9.2–4.9.3. Instructor note: 4.9.2 allows adjacent to entrance/within room OR at originating board. Thermostat must have definite OFF if used as isolator. Functional switching 4.9.3 is separate.

## Slide 35
SECTION 10 / WIRING RULES
35
ACT 27
Floor and ceiling heating
WORKBOOK PROMPTS
How are heating cable groups isolated?
Which location options apply?
What other protective device may be required?
◎
FIND THIS CLAUSE
4.10.3–4.10.5
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 27 — Floor and ceiling heating Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 4.10.3–4.10.5. Instructor note: 4.10.3 isolating switches may form part of control with definite OFF, within/near room or at originating board (trace heating exception). 4.10.5 calls for <=30mA RCD.

## Slide 36
SECTION 10 / WIRING RULES
36
ACT 28
Electricity converters
WORKBOOK PROMPTS
Where should isolation be positioned?
Can a programmable control provide isolation?
What if batteries are incorporated?
◎
FIND THIS CLAUSE
4.12.3–4.12.4
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 28 — Electricity converters Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 4.12.3–4.12.4. Instructor note: 4.12.4.1 independent manual isolator adjacent/on, lockable/open and in view of worker; no software bypass. 4.12.4.2 battery isolation adjacent batteries.

## Slide 37
SECTION 10 / WIRING RULES
37
04
MECHANICAL
Prevent an unexpected start
Electrical OFF is not always mechanical safety.
Notes: Ask students for a practical example before advancing to the clause-specific activities.

## Slide 38
SECTION 10 / WIRING RULES
38
ACT 29
Danger from unexpected movement
WORKBOOK PROMPTS
Describe a machine that could start unexpectedly.
What safety function should remain effective when maintained?
◎
FIND THIS CLAUSE
1.5.13
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 29 — Danger from unexpected movement Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 1.5.13. Instructor note: 1.5.13 is Part 1 protection against injury from mechanical movement. Supplement with 2.3.6 and 4.13.

## Slide 39
SECTION 10 / WIRING RULES
39
ACT 30
Motors: switching functions
WORKBOOK PROMPTS
List the functions needed for a motor.
Find the limited exceptions to separate isolation.
M
FIND THIS CLAUSE
4.13.1.1
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 30 — Motors: switching functions Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 4.13.1.1. Instructor note: Starter/stopping, emergency stopping, mechanical-maintenance isolation. The small-motor exception is rated no greater than 150VA; other exceptions plugged device and no exposed moving parts. Not blanket exemption from all switching.

## Slide 40
SECTION 10 / WIRING RULES
40
ACT 31
Motor isolation: breaking duty
WORKBOOK PROMPTS
Why is full-load current not enough?
What do manufacturer data and utilisation category tell you?
M
FIND THIS CLAUSE
4.13.1.2
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 31 — Motor isolation: breaking duty Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 4.13.1.2. Instructor note: Original incorrectly cites 4.13.1.1. Rating requirements in 4.13.1.2: interrupt locked-rotor/stall current. Without manufacturer data estimate AC 8× FLC, DC 4× FLC. M marking or AC-23/DC-23 category as appropriate. For grouped motors combine largest locked rotor plus other full load.

## Slide 41
SECTION 10 / WIRING RULES
41
ACT 32
Maintenance lockout
WORKBOOK PROMPTS
What would stop a worker being injured during servicing?
When is a lockable facility exception possible?
↔
FIND THIS CLAUSE
2.3.6.1
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 32 — Maintenance lockout Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.6.1. Instructor note: Locking off, lockable enclosure, warning notice. Lockable facility may be omitted only where shutdown device continuously under maintenance worker control. Mechanical, pneumatic energy may also need independent control.

## Slide 42
SECTION 10 / WIRING RULES
42
ACT 33
A safe shutdown device
WORKBOOK PROMPTS
How should it be operated?
How can a worker tell it is OFF?
What must not close accidentally?
◎
FIND THIS CLAUSE
2.3.6.2
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 33 — A safe shutdown device Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.6.2. Instructor note: Manual operation, clear/reliable OFF indication, prevention of accidental closure (impact/vibration).

## Slide 43
SECTION 10 / WIRING RULES
43
ACT 34
Where maintenance devices go
WORKBOOK PROMPTS
Which circuit should the shutdown device interrupt?
When is a remote shutdown device acceptable?
~
FIND THIS CLAUSE
2.3.6.3
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 34 — Where maintenance devices go Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.6.3. Instructor note: 2.3.6.3 installation in main circuit and able interrupt full load. May not interrupt all live conductors, unlike full isolation. Control-circuit exception needs supplementary safeguards; remote device must secure open. Workbook offers examples but misses major normative position.

## Slide 44
SECTION 10 / WIRING RULES
44
ACT 35
Identification and convenience
WORKBOOK PROMPTS
How can a maintainer identify the correct device?
Why might location matter as much as labelling?
◎
FIND THIS CLAUSE
2.3.6.4
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 35 — Identification and convenience Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.6.4. Instructor note: Devices for mechanical-maintenance shutdown placed and marked readily identifiable and convenient for intended use.

## Slide 45
SECTION 10 / WIRING RULES
45
ACT 36
Functional control is not isolation
WORKBOOK PROMPTS
Is an OFF pushbutton always safe for maintenance?
What types of devices are inappropriate for routine switching?
↔
FIND THIS CLAUSE
2.3.7.1–2.3.7.2
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 36 — Functional control is not isolation Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.7.1–2.3.7.2. Instructor note: Functional switching is operational only, not safety. Includes semiconductors/contactors. Disconnectors/fuses/links shall not be used for functional switching. Correct original overbroad wording about plugs/socket outlets.

## Slide 46
SECTION 10 / WIRING RULES
46
VISUAL REASONING / ISOLATION
Trace the supply path
Where do you draw the boundary between a control switch and true isolation?
SOURCE
ISOLATOR
CONTROLLER
LOAD
OFF at the controller does not prove the incoming supply is disconnected.
Notes: Functional switching does not necessarily provide isolation. Relate to 2.3.7, 2.3.2.2 and 4.13.

## Slide 47
SECTION 10 / WIRING RULES
47
05
SELECTION
A device must suit the duty
Poles, voltage, load breaking, environment and use.
Notes: Ask students for a practical example before advancing to the clause-specific activities.

## Slide 48
SECTION 10 / WIRING RULES
48
ACT 37
Unprotected consumer mains
WORKBOOK PROMPTS
What does “unprotected” actually mean here?
How is short-circuit risk reduced by the wiring system?
I
FIND THIS CLAUSE
2.5.1.2; 3.9.7.1.2
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 37 — Unprotected consumer mains Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.5.1.2; 3.9.7.1.2. Instructor note: Major correction: 2.5.1.2 rather than old 2.5.1.1(c). Consumer mains option (c) allows no upstream SC protective device if overload protection at board and installation meets 3.9.7.1.2 + distributor. Avoid old generalisation of substation 400A HRC fuse as universal.

## Slide 49
SECTION 10 / WIRING RULES
49
ACT 38
Sizing overload protection
WORKBOOK PROMPTS
How do design current, device rating and cable capacity relate?
What changes when a circuit-breaker limits maximum demand?
◎
FIND THIS CLAUSE
2.5.1.2; 2.5.3.3
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 38 — Sizing overload protection Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.5.1.2; 2.5.3.3. Instructor note: Teach Ib <= In <= Iz subject to standard selection and correction factors. 2.2.2(d) max demand by circuit-breaker limitation. Original attributes consumer-main rules incorrectly to 2.5.1.1 note 6; avoid distributor-era requirements.

## Slide 50
SECTION 10 / WIRING RULES
50
DESIGN DECISION
Protected or unprotected consumer mains?
Two paths through Clause 2.5.1.2. Which provisions must be satisfied?
POINT OF SUPPLY
WITH ORIGIN PROTECTION
WITHOUT ORIGIN SC DEVICE
Check protection coordination
Check 3.9.7.1.2 and distributor requirements
Unprotected does NOT mean “no design requirements”.
Notes: Cl 2.5.1.2 options (a) origin short-circuit + overload, (b) origin short circuit + switchboard overload, (c) switchboard overload with specially constructed mains 3.9.7.1.2; this is diagrammatic only.

## Slide 51
SECTION 10 / WIRING RULES
51
ACTIVITIES 39–42 / WORKED PROCESS
Find the table before the breaker
Correct method matters more than memorising an old example value.
1
Define cable
Conductor material, insulation and cores
2
Define installation
Enclosed / buried / touching / thermal insulation
3
Determine Iz
Select table, column and corrections
4
Coordinate
Check Ib, In, Iz and the device characteristics
Notes: Do not verify numerical current carrying capacities from AS/NZS 3000; those are in AS/NZS 3008.1.1. The user only supplied AS/NZS 3000. Ensure current licensed copy and installation method/correction factors before marking answers.

## Slide 52
SECTION 10 / WIRING RULES
52
ACT 39
Single-phase XLPE cable exercise
WORKBOOK PROMPTS
Locate the correct AS/NZS 3008 cable table.
Determine derated Iz before choosing In.
Record table number and installation method.
↗
FIND THIS CLAUSE
2.5.1.2 + AS/NZS 3008.1.1
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 39 — Single-phase XLPE cable exercise Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.5.1.2 + AS/NZS 3008.1.1. Instructor note: Original includes example tables and values based on AS/NZS 3008.1.1, which user has not supplied: do not certify numeric values. Ask students to use an accessible current authorised AS/NZS 3008.1.1, note loading factors, method and temp.

## Slide 53
SECTION 10 / WIRING RULES
53
ACT 40
Three-phase SDI cable exercise
WORKBOOK PROMPTS
Which three-phase grouping assumptions apply?
Locate the tabulated cable current.
Choose a suitable device using the correct derating.
↗
FIND THIS CLAUSE
2.5.1.2 + AS/NZS 3008.1.1
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 40 — Three-phase SDI cable exercise Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.5.1.2 + AS/NZS 3008.1.1. Instructor note: Original AS/NZS 3008 figures unverified; table and installation conditions must be checked from licensed/current source.

## Slide 54
SECTION 10 / WIRING RULES
54
ACT 41
Three-phase multicore exercise
WORKBOOK PROMPTS
Does multicore selection differ from single-core?
Find the installation-condition column.
Check protective-device coordination.
↗
FIND THIS CLAUSE
2.5.1.2 + AS/NZS 3008.1.1
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 41 — Three-phase multicore exercise Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.5.1.2 + AS/NZS 3008.1.1. Instructor note: Do not present original 16/25/35 mm2 numerics as confirmed AS/NZS 3008.1.1.

## Slide 55
SECTION 10 / WIRING RULES
55
ACT 42
Cable selection: mixed examples
WORKBOOK PROMPTS
Work from cable type, conductor material and method.
For an adjustable CB, what setting protects the cable?
↗
FIND THIS CLAUSE
2.5.1.2 + AS/NZS 3008.1.1
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 42 — Cable selection: mixed examples Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.5.1.2 + AS/NZS 3008.1.1. Instructor note: Original 240mm² aluminium 395 A/400 A adjustable CB: requires effective trip setting not exceeding Iz and correct factors. Do not assume 400 A fixed setting is acceptable.

## Slide 56
SECTION 10 / WIRING RULES
56
DEVICE SELECTION / PRACTICAL CHECK
Do not pick an isolator by amperes alone
The marked current rating is only one part of the selection.
POLES
Which active conductors must open?
VOLTAGE
Is the operational voltage suitable?
CURRENT
Does rated current cover design load?
DUTY
Can it break this kind of load?
CONDITIONS
IP, environment, access, lock-off
Notes: Utilisation class for AS/NZS 60947.3: AC-20 no-load, AC-21 mainly resistive, AC-22 mixed, AC-23 highly inductive/motor. Some switch-isolators are labelled M for locked rotor; ensure tested application suitability; verify manufacturer.

## Slide 57
SECTION 10 / WIRING RULES
57
ACT 43
Choose a suitable main isolator
WORKBOOK PROMPTS
Select pole arrangement and current rating.
Does this device need to break current on load?
Check the utilisation category.
◎
FIND THIS CLAUSE
2.3.2.2; 2.2.4
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 43 — Choose a suitable main isolator Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.2.2; 2.2.4. Instructor note: Use workbook 5 cases; old product codes are manufacturer and vintage specific. Device suitability checked to AS/NZS 60947.3 marking/data. AC-20 off-load, AC-21 resistive, AC-22 mixed, AC-23 motor/highly inductive; confirm operational voltage and power factor.

## Slide 58
SECTION 10 / WIRING RULES
58
ACT 44
Choose equipment isolators
WORKBOOK PROMPTS
Select device poles, duty rating and category.
For a motor, calculate the worst-case interruption duty.
◎
FIND THIS CLAUSE
2.3.2.2; 4.13.1.2
FIND → INTERPRET → RECORD
Use the book to justify your answer.
Notes: ACTIVITY 44 — Choose equipment isolators Standard: AS/NZS 3000:2018 with amendments 1–3 and Ruling 1, clause(s) 2.3.2.2; 4.13.1.2. Instructor note: Use workbook 5 cases; as for A43 check datasheet rated operational current, utilisation class, locked rotor, environmental rating and poles. For motors, 4.13.1.2 and AC-23 or appropriately marked M values.

## Slide 59
SECTION 10 / WIRING RULES
59
EXIT QUESTION
Choose the right switch for the right job
Explain your decision using a clause, the hazard and the device marking.
01
Does it need to isolate, control, or shut down for maintenance?
02
Are all required conductors disconnected?
03
Can the device carry AND interrupt the actual load?
04
Can someone operate it safely and identify it?
Notes: Suggested closing: ask pairs to critique an example of a correctly labelled general main switch, a motor isolator, and a cooking-appliance isolator.

## Slide 60
SECTION 10 / WIRING RULES
60
VERIFY IN THE SOURCE
Clauses, not old slide answers
The workbook may use different clause numbers and wording from the amended Wiring Rules.
PRIMARY SOURCE
AS/NZS 3000:2018 incorporating Amendments 1–3 and Ruling 1 (2024)
FOR NSW NETWORK CONNECTIONS
NSW Service and Installation Rules — April 2026
Cable sizing must be checked in AS/NZS 3008.1.1; figures in the old workbook were not independently validated.
Notes: Source notes: supplied PDF AS/NZS 3000:2018 A1 A2 A3 Ruling 1. NSW current SIR government URL https://www.energy.nsw.gov.au/nsw-plans-and-progress/regulation-and-policy/service-and-installation-rules . This slide is a reminder to read original standards; not a substitute.