## Slide 1
SECTION 7
CABLE SELECTION BASED ON
VOLTAGE DROP REQUIREMENTS

## Slide 2
CABLE SELECTION BASED ON VOLTAGE DROP REQUIREMENTS
L
  Voltage drop calculations
Topics
  Maximum length of cables
  Voltage drop tables in AS/NZS3008.1.1
  Cable selection
  AS/NZS3000 requirements

## Slide 3
L

## Slide 4
L

## Slide 5
L
5%
11.5V
20V

## Slide 6
L

## Slide 7
L

## Slide 8
L

## Slide 9
L

## Slide 10
L
x 1.155
x 0.866

## Slide 11
L
Page 91

## Slide 12
L
Use to find cable C.S.A
Use to find actual voltage drop

## Slide 13
L

## Slide 14
L
Page 108

## Slide 15
L
44.7 x 1.155 = 51.63 mV/A.m
9.71 x 1.155 = 11.22 mV/A.m
2.43 x 1.155 = 2.81 mV/A.m

## Slide 16
L
x 0.866 = 0.834 mV/A.m
x 0.866 = 0.221 mV/A.m
x 0.866 = 0.589 mV/A.m

## Slide 17
Page 108
L

## Slide 18
L
x 0.866 = 0.834 mV/A.m
x 0.866 = 0.221 mV/A.m
x 0.866 = 0.589 mV/A.m
(50mm2)
(70mm2)
(240mm2)

## Slide 19
L
Page 108
For table 40, highlight the following info and add the trefoil drawing for easy visual reference
Also take note at the bottom of each Vc table. To convert a 3 phase Vc to a single phase equivalent, you must use the multiplier x 1.155

## Slide 20
L
or in conduit
Page 109
For table 41, highlight the following info and add the laid flat drawing for easy visual reference.
This table is also used for cables in a wiring enclosure

## Slide 21
L
Page 110
For table 42, highlight the following info for multicore copper cables.
Note that Vc tables 43 to 45 are set out the same way but for ALUMINIUM conductors

## Slide 22
L
Vd = L x I x Vc
1000

## Slide 23
L
Use to find cable C.S.A
Use to find actual voltage drop

## Slide 24
L

## Slide 25
L

## Slide 26
L
Vd = L x I x Vc
1000
Vc = 6.49 mV/A.m (T42C6)
= 30 x 32 x 6.49
1000
= 6.23V

## Slide 27
L

## Slide 28
L

## Slide 29
L
Vd = L x I x Vc
1000
Vc = 2.55 mV/A.m (T41C8)
= 35 x 63 x 2.55
1000
= 5.622V

## Slide 30
L

## Slide 31
L
Vd = L x I x Vc
1000
Vc = 2.55 mV/A.m (T41C8)
= 35 x 63 x 2.55
1000
= 5.622V
Vd = L x I x Vc
1000
Vc = 9.71 mV/A.m (T42C6)
= 50 x 25 x 9.71
1000
= 12.138V
Vd total = 5.622 + 12.138
= 17.76V
Yes
Vd < 20V

## Slide 32
L

## Slide 33
L

## Slide 34
L
Vd = L x I x Vc
1000
Vc = 2.55 x 1.155
= 2.94 mV/A.m (T41C8)
= 35 x 63 x 2.94
1000
= 6.5V

## Slide 35
L

## Slide 36
L
Vd = L x I x Vc
1000
Vc = 2.55 x 1.155
= 2.94 mV/A.m (T41C8)
= 35 x 63 x 2.94
1000
= 6.5V
Vd = L x I x Vc
1000
Vc = 9.71 x 1.155
= 11.2 mV/A.m (T42C6)
= 50 x 25 x 11.2
1000
= 14V
Vd total = 6.5 + 14
= 20.5V (1φ)
No
Vd > 11.5V

## Slide 37
L
Vd = L x I x Vc
1000
Vc = 2.55 x 1.155
= 2.94 mV/A.m (single phase)
= 35 x 63 x 2.94
1000
= 6.5V
Example from previous activity:
Converting the Vc first:
Converting Vc in the equation:
Vd = L x I x Vc x 1.155
1000
= 35 x 63 x 2.55 x 1.155
1000
= 6.5V

## Slide 38
L

## Slide 39
L

## Slide 40
L
Vd = L x I x Vc
1000
Vc = 1.62 mV/A.m (T41C8)
= 25 x 80 x 1.62
1000
= 3.24V
V% = 3.24 x 100
400
= 0.81%

## Slide 41
L

## Slide 42
L
Vd = L x I x Vc
1000
Vc = 1.62 mV/A.m (T41C8)
= 25 x 80 x 1.62
1000
= 3.24V (3φ)
V% = 3.24 x 100
400
= 0.81%
Vd = L x I x Vc
1000
Vc = 6.49 x 1.155
= 7.49mV/A.m (T42C6)
= 50 x 25 x 7.49
1000
= 9.36V (1φ)
V% = 9.36 x 100
230
= 4.07%
V%T = V%CM + V%fsc
= 0.81 + 4.07
= 4.88%
Yes
V%T < 5%

## Slide 43
L

## Slide 44
L

## Slide 45
L
Vd = L x I x Vc
1000
Vc = 1.62 mV/A.m
(T41C8)
= 25 x 80 x 1.62
1000
= 3.24V (3φ)

## Slide 46
L

## Slide 47
L
Vd = L x I x Vc
1000
Vc = 1.62 mV/A.m
(T41C8)
= 25 x 80 x 1.62
1000
= 3.24V (3φ)
Vd = L x I x Vc
1000
Vc = 3.86 mV/A.m
(T42C6)
= 25 x 50 x 3.86
1000
= 4.825V (3φ)

## Slide 48
L

## Slide 49
L
Vd = L x I x Vc
1000
Vc = 1.62 mV/A.m
(T41C8)
= 25 x 80 x 1.62
1000
= 3.24V (3φ)
Vd = L x I x Vc
1000
Vc = 3.86 mV/A.m
(T42C6)
= 25 x 50 x 3.86
1000
= 4.825V (3φ)
Vd = L x I x Vc
1000
Vc = 15.6 x 1.155
= 18.018 mV/A.m
(T42C6)
= 50 x 20 x 18.018
1000
= 18.018V (1φ)
Vd = 3.24
√3
1.87 V (1φ)
22.7V
No
Vd = 4.825
√3
18.018V (1φ)
2.786 V (1φ)
+
+
22.7 > 11.5V
=

## Slide 50
L
Vc = 1000 x Vp
(L x I)

## Slide 51
L
Vc = 1000 x Vp
(L x I)
= 1000 x 14
(45 x 25)
= 12.44mV/A.m.

## Slide 52
L
≤ 12.44mV/A.m.

## Slide 53
L
Vc = 1000 x Vp
(L x I)
= 1000 x 14
(45 x 25)
= 12.44mV/A.m.
C.S.A = 4mm2 (9.71mV/A.m) T42C6

## Slide 54
L
Vp = 20 - 12
= 8V
8V
12V

## Slide 55
L
Vc = 1000 x Vp
(L x I)
= 1000 x 8
(30 x 32)
= 8.33mV/A.m.
Vp = 20 - 12
= 8V
8V
12V

## Slide 56
L
≤ 8.33mV/A.m.

## Slide 57
L
Vc = 1000 x Vp
(L x I)
= 1000 x 8
(30 x 32)
= 8.33mV/A.m.
Vp = 20 - 12
= 8V
8V
12V
C.S.A = 6mm2 (6.49mV/A.m) T42C6

## Slide 58
L

## Slide 59
L

## Slide 60
L
Vd = L x I x Vc
1000
Vc = 0.997 mV/A.m (T43C8)
= 55 x 150 x 0.997
1000
= 8.23V

## Slide 61
L
Vd = L x I x Vc
1000
Vc = 0.997 mV/A.m (T43C8)
= 55 x 150 x 0.997
1000
= 8.23V
Vp = 20 - 8.23
= 11.77V
Vc = 1000 x Vp
(L x I)
= 1000 x 11.77
(60 x 16)
= 12.26mV/A.m.

## Slide 62
L
≤12.26mV/A.m.

## Slide 63
L
Vd = L x I x Vc
1000
Vc = 0.997 mV/A.m (T43C8)
= 55 x 150 x 0.997
1000
= 8.23V
Vp = 20 - 8.23
= 11.77V
Vc = 1000 x Vp
(L x I)
= 1000 x 11.77
(60 x 16)
= 12.26mV/A.m.
C.S.A. = 4mm2 (9.71mV/A.m) T42 C6

## Slide 64
L

## Slide 65
L
Vc = 1000 x Vp
(L x I)
= 1000 x 8
(45 x 25)
= 7.11mV/A.m. (1 φ)
3 φ Vc= 7.11 x 0.866
= 6.15mV/A.m.

## Slide 66
L
≤ 6.15mV/A.m.

## Slide 67
L
Vc = 1000 x Vp
(L x I)
= 1000 x 8
(45 x 25)
= 7.11mV/A.m. (1 φ)
3 φ Vc= 7.11 x 0.866
= 6.15mV/A.m.
C.S.A. = 10mm2 (3.86mV/A.m) T42 C6

## Slide 68
L
Vc = 1000 x Vp x 0.866
(L x I)
= 1000 x 8 x 0.866
(45 x 25)
= 6.15 mV/A.m.
(3 phase value)
In activity 11, the 3 phase Vc after conversion was 6.15mV/A.m.
Example from previous activity:

## Slide 69
L
Vp = 11.5 - 6.9
= 4.6V
6.9 V
4.6 V

## Slide 70
L
Vp = 11.5 - 6.9
= 4.6V
6.9 V
4.6 V
Vc = 1000 x Vp
(L x I)
= 1000 x 4.6
(30 x 32)
= 4.79mV/A.m. (1 φ)
3 φ Vc= 4.79 x 0.866
= 4.14mV/A.m.

## Slide 71
L
≤ 4.14mV/A.m.

## Slide 72
L
Vp = 11.5 - 6.9
= 4.6V
6.9 V
4.6 V
Vc = 1000 x Vp
(L x I)
= 1000 x 4.6
(30 x 32)
= 4.79mV/A.m. (1 φ)
3 φ Vc= 4.79 x 0.866
= 4.14mV/A.m.
C.S.A. = 10mm2 (3.86mV/A.m) T42 C6

## Slide 73
L

## Slide 74
L

## Slide 75
L
Vd = L x I x Vc
1000
Vc = 2.55 x 1.155 = 2.95mV/A.m (T41C8)
= 15 x 80 x 2.95
1000
= 3.54V (1φ)
Vp = 11.5 - 3.54
= 7.96V
Vc = 1000 x Vp
(L x I)
= 1000 x 7.96
(40x(0.5x20))
= 19.9mV/A.m. (1φ)
3φ Vc= 19.9 x 0.866
= 17.23mV/A.m.

## Slide 76
L
≤ 17.23mV/A.m.

## Slide 77
L
Vd = L x I x Vc
1000
Vc = 2.55 x 1.155 = 2.95mV/A.m (T41C8)
= 15 x 80 x 2.95
1000
= 3.54V (1φ)
Vp = 11.5 - 3.54
= 7.96V
Vc = 1000 x Vp
(L x I)
= 1000 x 7.96
(40x(0.5x20))
= 19.9mV/A.m. (1φ)
3φ Vc= 19.9 x 0.866
= 17.23mV/A.m.
C.S.A. = 2.5mm2 (15.6mV/A.m) T42 C6

## Slide 78
L

## Slide 79
L

## Slide 80
L
Vd = L x I x Vc
1000
Vc = 2.55mV/A.m (T41C8)
= 20 x 63 x 2.55
1000
= 3.22V (3φ)
%p = 5% - 0.805%
= 4.195%
Vc = 1000 x Vp
(L x I)
= 1000 x 9.65
(55 x 22)
= 7.98mV/A.m. (1φ)
3 φ Vc= 7.98 x 0.866
= 6.91mV/A.m.
V% = 3.22 x 100
400
= 0.805%
Vp = 230 x 4.195 %
= 9.65V

## Slide 81
L
≤ 6.91mV/A.m.

## Slide 82
L
Vd = L x I x Vc
1000
Vc = 2.55mV/A.m (T41C8)
= 20 x 63 x 2.55
1000
= 3.22V (3φ)
%p = 5% - 0.805%
= 4.195%
Vc = 1000 x Vp
(L x I)
= 1000 x 9.65
(55 x 22)
= 7.98mV/A.m. (1φ)
3 φ Vc= 7.98 x 0.866
= 6.91mV/A.m.
V% = 3.22 x 100
400
= 0.805%
Vp = 230 x 4.195 %
= 9.65V
C.S.A. = 6mm2 (6.49mV/A.m) T41 C6

## Slide 83
L

## Slide 84
L
VC = 1.62 mV/A.m.

## Slide 85
L
Vd = L x I x Vc
1000
Vc = 1.62mV/A.m (T41C8)
= 25 x 100 x 1.62
1000
= 4.05V (3φ)

## Slide 86
L
Vc = 2.43 mV/A.m.

## Slide 87
L
Vd = L x I x Vc
1000
Vc = 1.62mV/A.m (T41C8)
= 25 x 100 x 1.62
1000
= 4.05V (3φ)
Vd = L x I x Vc
1000
Vc = 2.43 mV/A.m (T42C6)
= 45 x 63 x 2.43
1000
= 6.89V (3φ)
%p = 5% - 2.735%
= 2.265%
V% = 4.05+6.89 x 100
400
= 2.735%
Vp = 230 x 2.265 %
= 5.2V
Vc = 1000 x Vp
(L x I)
= 1000 x 5.2
(50 x 10)
= 10.4 mV/A.m. (1φ)
3φ Vc= 10.4 x 0.866
= 9.01 mV/A.m.

## Slide 88
≤ 9.01mV/A.m.
L

## Slide 89
L
Vd = L x I x Vc
1000
Vc = 1.62mV/A.m (T41C8)
= 25 x 100 x 1.62
1000
= 4.05V (3φ)
Vd = L x I x Vc
1000
Vc = 2.43 mV/A.m (T42C6)
= 45 x 63 x 2.43
1000
= 6.89V (3φ)
%p = 5% - 2.735%
= 2.265%
V% = 10.94 x 100
400
= 2.735%
Vp = 230 x 2.265 %
= 5.2V
Vc = 1000 x Vp
(L x I)
= 1000 x 5.2
(50 x 10)
= 10.4 mV/A.m. (1φ)
3φ Vc= 10.4 x 0.866
= 9.01 mV/A.m.
C.S.A. = 6.0 mm2 (6.49 mV/A.m) T42 C6

## Slide 90
L

## Slide 91
L
Vc = 2.55 mV/A.m.

## Slide 92
L
Vd = L x I x Vc
1000
Vc = 2.55 mV/A.m (T42C8)
= 15 x 63 x 2.55
1000
= 2.4 V (3φ)

## Slide 93
L
Vc = 9.71 mV/A.m.

## Slide 94
L
Vd = L x I x Vc
1000
Vc = 2.55 mV/A.m (T42C8)
= 15 x 63 x 2.55
1000
= 2.4 V (3φ)
Vd = L x I x Vc
1000
Vc = 9.71 x 1.155 = 11.2mV/A.m (T42C6)
= 15 x 25 x 11.2
1000
= 4.21 V (1φ)
VCM% = 2.4 x 100
400
= 0.6%
Vfsc%= 4.21 x 100
230
=1.83%
VSM%= 5-(0.6+1.83) = 2.57%
VSM 230 x 2.57% = 5.91 V
Vc = 1000 x Vp
(L x I)
= 1000 x 5.91
(50 x 40)
= 2.955 mV/A.m. (1φ)
3φ Vc= 2.995 x 0.866 = 2.55 mV/A.m.

## Slide 95
L
≤ 2.55 mV/A.m.

## Slide 96
L
Vd = L x I x Vc
1000
Vc = 2.55 mV/A.m (T42C8)
= 15 x 63 x 2.55
1000
= 2.4 V (3φ)
Vd = L x I x Vc
1000
Vc = 9.71 x 1.155 = 11.2mV/A.m (T42C6)
= 15 x 25 x 11.2
1000
= 4.21 V (1φ)
VCM% = 2.4 x 100
400
= 0.6%
Vfsc%= 4.21 x 100
230
=1.83%
VSM= 5-(0.6+1.83) = 2.57%
230 x 2.57% = 5.91 V
Vc = 1000 x Vp
(L x I)
= 1000 x 5.91
(50 x 40)
= 2.955 mV/A.m. (1φ)
3φ Vc= 2.995 x 0.866 = 2.55 mV/A.m.
C.S.A. = 16.0 mm2 (2.43mV/A.m) T42 C6

## Slide 97
L
L = 1000 x Vp
(Vc x I)

## Slide 98
L

## Slide 99
L

## Slide 100
L
L = 1000 x Vp
(Vc x I)
= 1000 x 12
(15.6 x 20)
= 38.46m
Vc = 15.6 mV/A.m (T42C6)

## Slide 101
L
Vp = 20 – (3 + 5)
= 12V

## Slide 102
L

## Slide 103
L
Vp = 20 – (3 + 5)
= 12V
L = 1000 x Vp
(Vc x I)
= 1000 x 12
(9.71 x 25)
= 49.43m
Vc = 9.71 mV/A.m (T42C6)

## Slide 104
L
Vp = 11.5 – (2 + 3)
= 6.5 V

## Slide 105
L

## Slide 106
L
Vp = 11.5 – (2 + 3)
= 6.5 V
L = 1000 x Vp
(Vc x I)
= 1000 x 6.5
(7.5 x 40)
= 21.67m
3φ Vc = 6.49 mV/A.m (T42C6)
1φ Vc = 6.49 x 1.155
= 7.5 mV/A.m

## Slide 107
L

## Slide 108
L

## Slide 109
L
Vd = L x I x Vc
1000
Vc = 0.623mV/A.m (T41C8)
= 40 x 200 x 0.632
1000
= 4.98V
VP = (20 – 4.98)
√3
= 8.67V (1φ)

## Slide 110
L

## Slide 111
L
Vd = L x I x Vc
1000
Vc = 0.623mV/A.m (T41C8)
= 40 x 200 x 0.632
1000
= 4.98V
VP = (20 – 4.98)
√3
= 8.67V (1φ)
3φ Vc = 28.6 mV/A.m (T41C6)
1φ Vc = 28.6 x 1.155
= 33.03 mV/A.m
L = 1000 x Vp
(Vc x I)
= 1000 x 8.67
(33.03 x 16)
= 16.41m

## Slide 112: END OF LESSON